## DC System
Project | 1X45MW Captive Power Plant, (Phase-1) At Jamshedpur, Jharkhand.,
Client | M/s. XXXX Ferro Pvt Ltd.,
Consultant | M/s. XXXX Engineering Consultants (I) Pvt. Ltd.
Document | Annexure-III Technical Data Sheet For DC System
S.No | Description | UOM | Tender Specification | Bidder Confirmation
I | Battery Charger
A | Construction
1 | Enclosure |  | Free Standing Cabinet, Floor Mounted Type, Sheet Steel Construction
a. | Material | mm | CRCA
b. | Sheet Steel Thickness | mm | 2 / 2.5
2 | Degree of Protection Within The Enclosure |  | IP42
3 | Degree of Protection Within The Switchgear |  | IP22
4 | Design Ambient Temperature | °C | 50
5 | Type of Cooling |  | Bidder To Specify
6 | Louvers With Wire Mesh |  | Required
7 | Working Zone Limits | mm | 750 - 1800
8 | Gaskets |  | Neoprene Gaskets
9 | Eye Bolts |  | Required
10 | Earthing Bus |  | 25x6mm Copper
11 | Base Channel with Anti Vibrating Pad |  | Required
12 | Cable Entry |  | Bottom
13 | Thickness of Cable Gland Plate | mm | 3
14 | Painting
a. | Inside |  | Bidder To Specify
b. | Outside |  | RAL 7035
c. | Paint Thickness | microns | ≥80
15 | Panel Dimensions (L x W x H) | mm | Bidder To Specify
16 | Panel Weight | Kgs | Bidder To Specify
B | Charger
1 | Type |  | Dual FCBC - SCR Based, 6 Pulse Full Wave Fully Controlled
2 | Quantity | Nos | 2
3 | Input Voltage | V AC | 415 ± 10%
4 | Input Frequency | Hz | 415 ± 10%
5 | Charger Capacity | V DC | 220
6 | Output Voltage - Nominal | V DC | 220 ± 5%
7 | Float Voltage | V DC | Bidder To Specify
8 | Boost Voltage | V DC | Bidder To Specify
9 | Load Voltage | V DC | 220 ± 5%
10 | Rated Output Current | A DC | 200
11 | Dropper Diode at Charger Output |  | Required
12 | Regulation | % | ± 1
13 | Ripple Content | % RMS | ≤ 1
14 | Efficiency | % | ≥ 85
15 | Insulation Class for All Magnetics |  | Class - "F"
16 | Temperature Rise for All Magnetics |  | Class - "B"
17 | Other Features
a. | Soft Start |  | Required
b. | Automatic Voltage Regulation |  | Required
c. | Automatic Float to Boost and Vice Versa |  | Required
d. | Charger Current Limiters |  | Required
e. | Battery Current Limiters |  | Required
C | Meters
1 | Charger-1 Meters |  | AC Input Voltmeter with Selector Switch
AC Input Ammeter with Selector Switch
DC Charger Output Voltmeter
DC Charger Output Ammeter
DC Voltmeter with Selector Switch (Battery)
DC Zero Center Ammeter (Battery)
DC Earth Leakage Ammeter (mA)
DC Load Voltmeter
DC Load Ammeter
2 | Charger-2 Meters |  | AC Input Voltmeter with Selector Switch
AC Input Ammeter with Selector Switch
DC Charger Output Voltmeter
DC Charger Output Ammeter
3 | AC Voltmeter & Ammeters |  | Digital Type, 240 Degree Scale, 96 Sq.mm, Class-0.5
4 | AC Meters - Make |  | AE / RISHAB / CONSERV
5 | DC Voltmeter & Ammeters |  | Digital Type, 240 Degree Scale, 96 Sq.mm, Class-0.5
6 | DC Meters - Make |  | AE / RISHAB / CONSERV
D | Indications
1 | Mains AC Supply ON (R, Y, B) |  | Required
2 | Float Charging ON for Both FCBC-1 & 2 |  | Required
3 | Boost Charging ON for Both FCBC-1 & 2 |  | Required
4 | FCBC-1 Fail |  | Required
5 | FCBC-2 Fail |  | Required
6 | Battery Fully Discharged |  | Required
E | Protections
1 | AC Input Isolation MCCB for Both FCBC-1 & 2 |  | Required
2 | Fast Acting Semiconductor Fuses for Rectifier Bridge for Both FCBC-1 & 2 |  | Required
3 | DC Over Voltage Protection for Both FCBC-1 & 2 |  | Required
4 | Charger Overload Protection for Both FCBC-1 & 2 |  | Required
5 | Charger Current Limit for Both FCBC-1 & 2 |  | Required
6 | Battery Current Limit |  | Required
7 | Blocking Diode for Both FCBC-1 & 2 |  | Required
8 | DC Output Isolation MCCB for Both FCBC-1 & 2 |  | Required
9 | Battery Input Isolation MCCB |  | Required
F | Annunciations
1 | SCR Fuse Failure |  | Required
2 | Charger Overload |  | Required
3 | Charger Fail/Trip |  | Required
4 | Battery Fully Discharged |  | Required
5 | AC Input Under Voltage |  | Required
6 | DC Under Voltage |  | Required
7 | DC Over Voltage |  | Required
8 | Thyristor/Diode Failure |  | Required
9 | DC Earth Leakage |  | Required
10 | AC Input Fuse Blown-off / MCCB Trip |  | Required
11 | DC Output Fuse Blown-off / MCCB Trip |  | Required
12 | DC Battery Fuse Blown-off / MCCB Trip |  | Required
13 | Filter Capacitor Fuse Blown-off |  | Required
14 | Short Circuit |  | Required
15 | Reverse Polarity |  | Required
16 | Battery Current Limiter |  | Required
G | Power & Control Circuit
1 | Panel Wiring
a. | Type / Insulation |  | FRLS PVC
b. | Voltage Grade | V | 1100
c. | Material |  | Stranded Copper
d. | Power Circuit | Sq.mm | Bidder To Specify
e. | Control Circuit | Sq.mm | 1.5
f. | Wires Identified at Both Ends With Ferrules |  | Required
g. | Colour Coding |  | AC Circuit: Red, Yellow, Blue, Black DC Circuit: Red, Black Control Circuit: Grey
2 | Terminal Blocks
a. | Power Terminal Blocks |  | Stud Type, Nut Driver Operated
b. | Control Terminal Blocks |  | Bidder To Specify
b. | 20 % Spare Terminal Blocks |  | Required
c. | Terminal Shroud With Phase Barriers (Power & Control) |  | Required
H | Accessories
1 | Space Heater |  | Required
2 | Plug Socket |  | Required
3 | Illumination Lamp |  | Required
II | Battery
A | General
1 | Battery Type |  | Maintenance Free VRLA Battery
2 | Battery Rating | AH | 500
3 | Quantity | Sets | 2
4 | Battery Model |  | Bidder To Specify
5 | Number of Cells | Nos | 110
6 | Load Duty Cycle | Hours | 10
7 | AH Efficiency | % | ≥ 95
8 | WH Efficiency | % | ≥ 85
9 | Loss of Capacity Due to Self Discharge / Week | % | < 0.5
10 | Cycle Life of Battery @ 27°C
a. | At 20% Depth of Discharge |  | Bidder To Specify
b. | At 50% Depth of Discharge |  | Bidder To Specify
c. | At 80% Depth of Discharge |  | Bidder To Specify
11 | Expected Life of Battery | Years | Minimum 20 or Better
12 | Maximum Allowable Ambient Temperature |  | Bidder To Specify
13 | Recommended Maximum Period of Storage |  | Bidder To Specify
B | Electrical Parameters
1 | Voltage / Cell | V DC | 2
2 | End Cell Voltage | V DC | 1.85
3 | Float Voltage | V DC | Bidder To Specify
4 | Boost Voltage | V DC | Bidder To Specify
5 | Current Limit | V DC | Bidder To Specify
6 | Voltage Ripple Allowable | % RMS | ≤ 1.5
7 | Cell Internal Resistance - Fully Charged Condition | milli ohms | Bidder To Specify
8 | Battery Internal Resistance - Fully Charged Condition | milli ohms | Bidder To Specify
9 | Time Required for Boost Charge From Fully Discharged Condition to 100% Charged Condition |  | 10 Hours
10 | Short Circuit Current Capacity @ Battery Terminals | kA | Bidder To Specify
11 | Short Circuit Withstand Time @ Battery Terminals | Sec | Bidder To Specify
C | Construction
1 | Cell Dimensions (L x W x H) | mm | Bidder To Specify
2 | Cell Weight | Kgs | Bidder To Specify
3 | Battery Bank Dimensions (L x W x H) | mm | Bidder To Specify
4 | Battery Bank Weight | Kgs | Bidder To Specify
5 | Container Material |  | Polypropylene Co-polymer
6 | Type of Separators |  | Bidder To Specify
7 | Type of Positive & Negative Plates |  | Flat Pasted
8 | Type of Terminal Connectors |  | Bidder To Specify
9 | Material of Tray / Racks |  | MS Coated With Acid Resistant Coating
10 | Self Re-Sealing Safety Vent Valves |  | Required
C | Battery Isolation Box
1 | Battery Isolation Box |  | Required
2 | Quantity | Nos | 2
3 | Enclosure Material |  | CRCA
4 | Enclosure Thickness | mm | ≥2
5 | Paint Shade |  | Required
6 | Fuse Fail Protection |  | Required
III | DCDB
A | Construction
1 | Enclosure |  | Free Standing Cabinet, Floor Mounted Type, Sheet Steel Construction
a. | Material | mm | CRCA
b. | Sheet Steel Thickness | mm | 2
2 | Degree of Protection Within The Enclosure |  | IP54
3 | Degree of Protection Within The Switchgear |  | IP22
4 | Design Ambient Temperature | °C | 50
5 | Type of Cooling |  | Bidder To Specify
6 | Louvers With Wire Mesh |  | Required
7 | Working Zone Limits | mm | 400 - 1800
8 | Gaskets |  | Neoprene Gaskets
9 | Eye Bolts |  | Required
10 | Earthing Bus |  | 25x6mm Copper
11 | Base Channel with Anti Vibrating Pad |  | Required
12 | Cable Entry |  | Bottom
13 | Thickness of Cable Gland Plate | mm | 3
14 | Painting
a. | Inside |  | Bidder To Specify
b. | Outside |  | RAL 7035
c. | Paint Thickness | microns | ≥80
15 | Panel Dimensions (L x W x H) | mm | Bidder To Specify
16 | Panel Weight | Kgs | Bidder To Specify
B | Incomer & Bus Coupler Module
1 | Incomer & Bus Coupler Breakers |  | MCCB
2 | Breaker Rating | Amps | 250
3 | Key Interlock |  | Required
4 | DC Voltmeter & Ammeters |  | Required
5 | Indications |  | ON / OFF / TRIP
C | Outgoing Feeders
1 | Outgoing Feeders |  | MCCB & MCB
2 | Breaker Rating | Amps | As Per DC Distribution SLD
IV | Delivery Schedule
1 | Delivery Schedule |  | Bidder To Specify