## DC System
Project | 1X45MW Captive Power Plant, (Phase-1) At Jamshedpur, Jharkhand.,
Client | M/s. Gajanan Ferro Pvt Ltd.,
Consultant | M/s. Aquatherm Engineering Consultants (I) Pvt. Ltd.
Document | Annexure-III Technical Data Sheet For DC System
S.No | Description | UOM | Tender Specification | Bidder Confirmation
I | Battery Charger
A | Construction
1 | Enclosure |  | Free Standing Cabinet, Floor Mounted Type, Sheet Steel Construction | Complies.
a. | Material | mm | CRCA | Complies.
b. | Sheet Steel Thickness | mm | 2 / 2.5 | Complies.
2 | Degree of Protection Within The Enclosure |  | IP42 | Complies.
3 | Degree of Protection Within The Switchgear |  | IP22 | - - - - -
4 | Design Ambient Temperature | °C | 50 | Complies.
5 | Type of Cooling |  | Bidder To Specify | Natural (OR) Forced Air Cooling
6 | Louvers With Wire Mesh |  | Required | Complies.
7 | Working Zone Limits | mm | 750 - 1800 | Complies.
8 | Gaskets |  | Neoprene Gaskets | PU Form Gaskets will be Provided
9 | Eye Bolts |  | Required | Complies.
10 | Earthing Bus |  | 25x6mm Copper | Complies.
11 | Base Channel with Anti Vibrating Pad |  | Required | Complies.
12 | Cable Entry |  | Bottom | Complies.
13 | Thickness of Cable Gland Plate | mm | 3 | Complies.
14 | Painting
a. | Inside |  | Bidder To Specify | INT : Glossy White
b. | Outside |  | RAL 7035 | Complies.
c. | Paint Thickness | microns | ≥80 | Min 80 – 100 Microns
15 | Panel Dimensions (L x W x H) | mm | Bidder To Specify | Noted & Considered, In detail will be provided during order execution
16 | Panel Weight | Kgs | Bidder To Specify | Will be provided during order execution
B | Charger
1 | Type |  | Dual FCBC - SCR Based, 6 Pulse Full Wave Fully Controlled | Complies. DFCBC-2CL Provided as per TSP.
2 | Quantity | Nos | 2 | Noted.
3 | Input Voltage | V AC | 415 ± 10% | Complies.
4 | Input Frequency | Hz | 415 ± 10% | 50Hz ± 5%
5 | Charger Capacity | V DC | 220 | Complies.
6 | Output Voltage - Nominal | V DC | 220 ± 5% | Complies.
7 | Float Voltage | V DC | Bidder To Specify | 247.5V DC (110 X 2.25V/Cell) adjustable by +2%, -5%
8 | Boost Voltage | V DC | Bidder To Specify | 253.0V DC (110 X 2.3V/Cell) adjustable by +2%, -5%
9 | Load Voltage | V DC | 220 ± 5% | 220V DC +/- 5%
10 | Rated Output Current | A DC | 200 | Complies.
11 | Dropper Diode at Charger Output |  | Required | Complies.
12 | Regulation | % | ± 1 | Complies.
13 | Ripple Content | % RMS | ≤ 1 | Complies.
14 | Efficiency | % | ≥ 85 | Complies.
15 | Insulation Class for All Magnetics |  | Class - "F" | Complies.
16 | Temperature Rise for All Magnetics |  | Class - "B" | Complies.
17 | Other Features
a. | Soft Start |  | Required | Complies.
b. | Automatic Voltage Regulation |  | Required | Complies.
c. | Automatic Float to Boost and Vice Versa |  | Required | Complies.
d. | Charger Current Limiters |  | Required | Complies.
e. | Battery Current Limiters |  | Required | Complies.
C | Meters
1 | Charger-1 Meters |  | AC Input Voltmeter with Selector Switch | Complies.
|  |  | AC Input Ammeter with Selector Switch | Complies.
|  |  | DC Charger Output Voltmeter | Complies.
|  |  | DC Charger Output Ammeter | Complies.
|  |  | DC Voltmeter with Selector Switch (Battery) | Complies.
|  |  | DC Zero Center Ammeter (Battery) | Complies.
|  |  | DC Earth Leakage Ammeter (mA) | Complies.
|  |  | DC Load Voltmeter | Complies.
|  |  | DC Load Ammeter | Complies.
2 | Charger-2 Meters |  | AC Input Voltmeter with Selector Switch | Complies.
|  |  | AC Input Ammeter with Selector Switch | Complies.
|  |  | DC Charger Output Voltmeter | Complies.
|  |  | DC Charger Output Ammeter | Complies.
3 | AC Voltmeter & Ammeters |  | Digital Type, 240 Degree Scale, 96 Sq.mm, Class-0.5 | Noted & 1.0% Accuracy will be Provided.
4 | AC Meters - Make |  | AE / RISHAB / CONSERV | Complies.
5 | DC Voltmeter & Ammeters |  | Digital Type, 240 Degree Scale, 96 Sq.mm, Class-0.5 | Noted & 1.0% Accuracy will be Provided.
6 | DC Meters - Make |  | AE / RISHAB / CONSERV | Complies.
D | Indications
1 | Mains AC Supply ON (R, Y, B) |  | Required | Complies.
2 | Float Charging ON for Both FCBC-1 & 2 |  | Required | Complies.
3 | Boost Charging ON for Both FCBC-1 & 2 |  | Required | Complies.
4 | FCBC-1 Fail |  | Required | Complies.
5 | FCBC-2 Fail |  | Required | Complies.
6 | Battery Fully Discharged |  | Required | Complies.
E | Protections
1 | AC Input Isolation MCCB for Both FCBC-1 & 2 |  | Required | Complies.
2 | Fast Acting Semiconductor Fuses for Rectifier Bridge for Both FCBC-1 & 2 |  | Required | Complies.
3 | DC Over Voltage Protection for Both FCBC-1 & 2 |  | Required | Complies.
4 | Charger Overload Protection for Both FCBC-1 & 2 |  | Required | Complies.
5 | Charger Current Limit for Both FCBC-1 & 2 |  | Required | Complies.
6 | Battery Current Limit |  | Required | Complies.
7 | Blocking Diode for Both FCBC-1 & 2 |  | Required | Complies.
8 | DC Output Isolation MCCB for Both FCBC-1 & 2 |  | Required | Complies.
9 | Battery Input Isolation MCCB |  | Required | Complies.
F | Annunciations
1 | SCR Fuse Failure |  | Required | Complies.
2 | Charger Overload |  | Required | Complies.
3 | Charger Fail/Trip |  | Required | Complies.
4 | Battery Fully Discharged |  | Required | Complies.
5 | AC Input Under Voltage |  | Required | Complies.
6 | DC Under Voltage |  | Required | Complies.
7 | DC Over Voltage |  | Required | Complies.
8 | Thyristor/Diode Failure |  | Required | SCR/Thyristor Fuse Fail Provided. Diode Fail can't be Complied.
9 | DC Earth Leakage |  | Required | Complies.
10 | AC Input Fuse Blown-off / MCCB Trip |  | Required | Complies.
11 | DC Output Fuse Blown-off / MCCB Trip |  | Required | Complies.
12 | DC Battery Fuse Blown-off / MCCB Trip |  | Required | Complies.
13 | Filter Capacitor Fuse Blown-off |  | Required | Complies.
14 | Short Circuit |  | Required | Complies.
15 | Reverse Polarity |  | Required | Complies.
16 | Battery Current Limiter |  | Required | Complies.
G | Power & Control Circuit
1 | Panel Wiring
a. | Type / Insulation |  | FRLS PVC | Complies.
b. | Voltage Grade | V | 1100 | Complies.
c. | Material |  | Stranded Copper | Complies.
d. | Power Circuit | Sq.mm | Bidder To Specify | Cable of Suitable Size (Sqmm) will be used for wiring of Battery Charger
e. | Control Circuit | Sq.mm | 1.5 | Cable of Suitable Size (Sqmm) will be used for wiring of Battery Charger
f. | Wires Identified at Both Ends With Ferrules |  | Required | Complies.
g. | Colour Coding |  | AC Circuit: Red, Yellow, Blue, Black DC Circuit: Red, Black Control Circuit: Grey | Complies.
2 | Terminal Blocks
a. | Power Terminal Blocks |  | Stud Type, Nut Driver Operated | Nut Driver Operated
b. | Control Terminal Blocks |  | Bidder To Specify | Complies.
b. | 20 % Spare Terminal Blocks |  | Required | Complies.
c. | Terminal Shroud With Phase Barriers (Power & Control) |  | Required | Complies.
H | Accessories
1 | Space Heater |  | Required | Complies.
2 | Plug Socket |  | Required | Complies.
3 | Illumination Lamp |  | Required | Complies.
II | Battery
A | General
1 | Battery Type |  | Maintenance Free VRLA Battery | Complied
2 | Battery Rating | AH | 500 | 110 V - 510 AH to 1.75 ECV @ C10 at 27°C
3 | Quantity | Sets | 2 | Complied
4 | Battery Model |  | Bidder To Specify | IP2013
5 | Number of Cells | Nos | 110 | Complied
6 | Load Duty Cycle | Hours | 10 | 1.Load Duty Cycle not our scope of work 2.We will validate battery sizing based on load currents in terms of duration
7 | AH Efficiency | % | ≥ 95 | Above 95%
8 | WH Efficiency | % | ≥ 85 | Above 85%
9 | Loss of Capacity Due to Self Discharge / Week | % | < 0.5 | < 1% of rated capacity per Week @ 27°C
10 | Cycle Life of Battery @ 27°C
a. | At 20% Depth of Discharge |  | Bidder To Specify | 4000 cycles at 20% Depth of Discharge(DOD)
b. | At 50% Depth of Discharge |  | Bidder To Specify | 2000 cycles at 50% Depth of Discharge(DOD)
c. | At 80% Depth of Discharge |  | Bidder To Specify | 1200 cycles at 80% DOD
11 | Expected Life of Battery | Years | Minimum 20 or Better | Design float life of up to 20 years @ 27°C
12 | Maximum Allowable Ambient Temperature |  | Bidder To Specify | 60°C continuous and 70°C short time
13 | Recommended Maximum Period of Storage |  | Bidder To Specify | 6 months from the date of dispatch before first use and battery should be stored in a covered area at 27°C.
B | Electrical Parameters
1 | Voltage / Cell | V DC | 2 | COMPLIES
2 | End Cell Voltage | V DC | 1.85 | Complied with 1.85ECV & Designe ECV at 1.75ECV
3 | Float Voltage | V DC | Bidder To Specify | 2.23 - 2.25 Volts per Cell @ 27°C
4 | Boost Voltage | V DC | Bidder To Specify | 2.30 - 2.32 Volts per Cell @ 27°C
5 | Current Limit | V DC | Bidder To Specify | 51 Amps minumum to 102 Amps maximum.
6 | Voltage Ripple Allowable | % RMS | ≤ 1.5 | <2% of the RMS. Value
7 | Cell Internal Resistance - Fully Charged Condition | milli ohms | Bidder To Specify | 0.450 (mΩ)
8 | Battery Internal Resistance - Fully Charged Condition | milli ohms | Bidder To Specify | NA
9 | Time Required for Boost Charge From Fully Discharged Condition to 100% Charged Condition |  | 10 Hours | 8 Hrs from 0-90% Sate of Charge (SOC)(or) 16 Hrs from 0-100% State of Charge
10 | Short Circuit Current Capacity @ Battery Terminals | kA | Bidder To Specify | 4546 Amps
11 | Short Circuit Withstand Time @ Battery Terminals | Sec | Bidder To Specify | milli seconds
C | Construction
1 | Cell Dimensions (L x W x H) | mm | Bidder To Specify | (198.5 x 532 x 107.8) mm Approx.
2 | Cell Weight | Kgs | Bidder To Specify | 30.4 kg. Approx
3 | Battery Bank Dimensions (L x W x H) | mm | Bidder To Specify | Please Refer Approved GA Drawing
4 | Battery Bank Weight | Kgs | Bidder To Specify | Please Refer Approved GA Drawing
5 | Container Material |  | Polypropylene Co-polymer | Complied to Polypropylene co-polymer.
6 | Type of Separators |  | Bidder To Specify | Highly absorbent Micro porous spun glass matrix.(AGM)
7 | Type of Positive & Negative Plates |  | Flat Pasted | Complied to Flat Pasted
8 | Type of Terminal Connectors |  | Bidder To Specify | Lead coated Heavy duty copper strips
9 | Material of Tray / Racks |  | MS Coated With Acid Resistant Coating | Batteries shall be supplied in self-stackable MS racks coated with acid resistant powder coating.
10 | Self Re-Sealing Safety Vent Valves |  | Required | Complied
C | Battery Isolation Box
1 | Battery Isolation Box |  | Required | Complies.
2 | Quantity | Nos | 2 | Complies.
3 | Enclosure Material |  | CRCA | Complies.
4 | Enclosure Thickness | mm | ≥2 | Complies.
5 | Paint Shade |  | Required | Complies.
6 | Fuse Fail Protection |  | Required | Battery I/P MCCB Trip/Off Indication & Alarm already Provided in Charger.
III | DCDB
A | Construction
1 | Enclosure |  | Free Standing Cabinet, Floor Mounted Type, Sheet Steel Construction | Free Standing Cabinet, Floor Mounted Type, SheetSteel Construction and Non-Compartmentalized.
a. | Material | mm | CRCA | Complies.
b. | Sheet Steel Thickness | mm | 2 | Complies.
2 | Degree of Protection Within The Enclosure |  | IP54 | Complies.
3 | Degree of Protection Within The Switchgear |  | IP22
4 | Design Ambient Temperature | °C | 50 | Complies.
5 | Type of Cooling |  | Bidder To Specify | Natural Air Cooling
6 | Louvers With Wire Mesh |  | Required | Complies.
7 | Working Zone Limits | mm | 400 - 1800 | Complies.
8 | Gaskets |  | Neoprene Gaskets | PU Form Gaskets will be Provided
9 | Eye Bolts |  | Required | Complies.
10 | Earthing Bus |  | 25x6mm Copper | Complies.
11 | Base Channel with Anti Vibrating Pad |  | Required | Complies.
12 | Cable Entry |  | Bottom | Complies.
13 | Thickness of Cable Gland Plate | mm | 3 | Complies.
14 | Painting
a. | Inside |  | Bidder To Specify | Interior: Glossy White
b. | Outside |  | RAL 7035 | Complies.
c. | Paint Thickness | microns | ≥80 | Min 80 – 100 Microns
15 | Panel Dimensions (L x W x H) | mm | Bidder To Specify | During Detailed Engineering Stage (Drawing Approval)
16 | Panel Weight | Kgs | Bidder To Specify | During Detailed Engineering Stage (Drawing Approval)
B | Incomer & Bus Coupler Module
1 | Incomer & Bus Coupler Breakers |  | MCCB | Complies.
2 | Breaker Rating | Amps | 250 | Complies.
3 | Key Interlock |  | Required | Complies.
4 | DC Voltmeter & Ammeters |  | Required | Complies.
5 | Indications |  | ON / OFF / TRIP | Complies. ON, TRIP/OFF Will be Provided.
C | Outgoing Feeders
1 | Outgoing Feeders |  | MCCB & MCB | Complies.
2 | Breaker Rating | Amps | As Per DC Distribution SLD | Complies.
IV | Delivery Schedule
1 | Delivery Schedule |  | Bidder To Specify