GENERAL DESCRIPTION

The Battery Charger Unit basically consists of Two Float cum Boost Chargers. Each Float cum Boost Charger is capable to supply the load Battery charging requirements. In normal mode of operation, the Battery assembly is Float charged by both the chargers while feeding the DC load thus operating in parallel and sharing the total load. When FCBC-1 fails, the other charger FCBC-2 comes into operation and takes care of the load and battery trickle charging current.

Both the Chargers basically consist of Input Transformer, Rectifier Bridge, Filter Circuit and Charger Control Board. The Input Transformer steps down the AC Input Voltage to the required AC level. The Rectifier is built with SCRs, which are connected to Full Wave Full Controlled configuration. The Rectifier Bridge convert stepped down AC into regulated DC. The Filter Circuit eliminates AC ripples in DC Output. The Charger Control Board provides the gate pulses to SCRs. Voltage and Current Feedback circuits provide error signals to the charger control board to achieve voltage regulation and current limit.

AC Ammeter and AC Voltmeter with selector switch is provided to monitor the AC Input Current and AC Input Voltage in each charger individually. DC output Ammeter is provided to monitor the DC output current in each charger individually. One common voltmeter is provided with selector switch to monitor the FCBC-1, FCBC-2, Battery and load voltages, one DC Ammeter is provided to monitor charge/discharge current of the battery. Blocking diode is provided at the output of each charger to prevent power dissipation in the charger when the battery is supplying to load.

The Battery Chargers, FCBC-1 & FCBC-2 are housed in Single Cabinet of free-standing sheet steel construction. The cabinets are provided with front & rear doors for accessibility. All AC Input and DC Output Switchgear of FCBC-1 & FCBC-2 are provided inside the cubicle at appropriate place for easy accessibility and maintenance. Panel Meters, Meter Selector Switches and Alarm Annunciator (Fascia Display Unit) is provided on the front panel of the cabinet and also cable entry is provided at the front bottom of the cabinets. By opening the front door, one can reach the termination easily.

IMP NOTE: 1) The Battery Chargers, FCBC-1; FCBC-2 are housed in Suitable Cabinets of

Free standing sheet steel construction.

2) PVC FRLS Cables / Suitable Bus bars will be used for Battery Charger Wiring.

* * * * *

TECHNICAL SPECIFICATION OF THE BATTERY CHARGER

- SCHEME	:	DUAL FLOAT CUM BOOST CHARGER – 2CL WITH DD CKT

- TYPE	:	FULL WAVE, FULL CONTROLLED

- RATING	:	220V/200A DFCBC (Suitable for 220V- 510AH VRLA Battery of 110 Cells)

- AC INPUT

  - Voltage	:	415VAC ± 10%

  - Frequency	:	50Hz ± 5%

  - Phase, Wire	:	3 Phase, 4 Wire

- DC OUTPUT

- Float cum Boost Charger – 1 & 2

  - Nominal Voltage	:	220V DC

  - Float Voltage	:	247.5V DC (110 X 2.25V/Cell) adjustable by +2%, -5%

  - Boost Voltage	:	253.0V DC (110 X 2.3V/Cell) adjustable by +2%, -5%

  - Regulation	:	Better than ±1% of set value

  - Ripple	:	< 1% RMS

  - Current	:	250A

- System output voltage   :	Maximum 220V ± 5% DC (After Dropper Diode Circuit)

- Efficiency	:	Better than 85% at Full load.

- METERS	:	Following Analogue Type Meters of 96 mm X 96 mm with 240D

Deflection and Accuracy class 1.0% will be provided in the system			for measuring the respective parameters:

  - AC Voltmeter & AC Ammeter with Selector Switch for both FCBC – 1 & 2

  - DC Voltmeter for both FCBC – 1 & 2

  - DC Ammeter for both FCBC – 1 & 2

  - Battery Charge/Discharge Ammeter

  - DC Voltmeter with Selector Switch at Battery

  - DC Load Ammeter

  - DC Load Voltmeter

  - DC Earth Leakage Ammeter (mA)

- INDICATIONS	:	I. Clustered LED Lamps will be provided for the following			condition [For FCBC-I & FCBC-II]:

    - AC Mains ON (R, Y, B)” (Common AC I/P Source)

    - Float ON (FCBC – 1 & 2)

    - Boost ON (FCBC – 1 & 2)

    - Charger ON (FCBC – 1 & 2)

- Alarm Annunciator (Fascia Display Unit) will be provided with an audio alarm for following abnormal conditions:

  - AC I/P Supply Fail / AC Mains Fail

  - AC I/P Under Voltage

  - FCBC – 1 Fail

  - FCBC – 2 Fail

  - FCBC – 1 Rectifier Fuse Fail

  - FCBC – 2 Rectifier Fuse Fail

  - FCBC – 1 Filter Cap Fuse Fail

  - FCBC – 2 Filter Cap Fuse Fail

  - FCBC – 1 Overload

  - FCBC – 2 Overload

  - FCBC – 1 AC I/P MCCB Trip/OFF

  - FCBC – 2 AC I/P MCCB Trip/OFF

  - FCBC – 1 DC Output MCCB Trip/OFF

  - FCBC – 2 DC Output MCCB Trip/OFF

  - Battery I/P MCCB Trip/OFF

  - Battery Current Limiter

  - Battery Short Circuit

  - Battery Reverse Polarity

  - DC/Load Over Voltage

  - DC/load Under Voltage

  - DC Earth Fault

  - 2 Nos Spare Windows

- Note: “Group Alarm” / “Charger Trouble” Potential Free Contacts for Remote Alarm are provided and same will be wired to a terminal block for Customer / Remote connection.

  - PROTECTIONS	:	Following Protections will be provided in the system:

- AC Input MCCB (With O/L & S/C Protection) for both               FCBC – 1 & 2

- DC Output MCCB for both FCBC – 1 & 2

- Fast acting Semiconductor Fuses for Rectifier Bridge for both FCBC – 1 & 2

- DC OV Cutback Protection for both FCBC – 1 & 2

- Charger Overload Protection for both FCBC – 1 & 2

- Battery Input MCCB

- Extra Separate Wall Mountable Battery Isolation Box (3P MCCB) with IP-42 Protection & Sheet Thickness of 2.0mm

- DC Under Voltage Protection

- DC Earth Fault Protection

- Surge Suppressor Circuit Protection (Through Amara Raja make PCB)

- Blocking Diode for both FCBC – 1 & 2

  - CONTROLS & SWITCHES	:	Following Control & Switches will be provided in the system

- AC Input MCCB (With O/L & S/C Protection) for both FCBC – 1 & 2

- DC Output MCCB for both FCBC – 1 & 2

- Auto/Manual Float/Manual Boost Selector Switch

- Float & Boost Voltage Adjust POTs for both FCBC–1& 2

- DC Voltmeter Selector Switch

- AC Volt – Amp Selector Switch

- Test, Accept & Reset Push Button

- Fan Power Supply ON/OFF Toggle Switch (If Fans Considered)

- Door Lamp, Heaters and Socket Power Supply ON/OFF Toggle Switch

  - SPECIAL FEATURES	:       The following features are provided in the system.

- Soft starts on DC side.

- Class-F insulation with Class-B Temp limits for all Magnetics

- Automatic Voltage Regulation using Digital Control Logic

- Automatic Float to Boost and vice versa Change Over based on Current drawn by Battery

- Filter Circuit to Limit Ripple

- Charger Current Limiting

- Battery Current Limiting

- Built in Auto Phase Reversal Operation

  - TRANSDUCERS	:	Following 4–20mA (Single I/P & Dual O/P) Transducers will be		Provided in Charger:

- DC Voltage Transducers – 3 No’s (For FCBC - 1 O/P, FCBC – 2 O/P & Battery Path)

- DC Current Transducers – 2 No’s (For FCBC – 1 O/P, FCBC – 2 O/P)

  - GENERAL

- Cabinet	:	Free Standing Cabinet, Floor Mounted Type, Sheet Steel,			Construction, Easy Access for Installation &				Commissioning. Cable Entry at Bottom.

- Sheet Thickness	:	2.0mm for non-load bearing sections and 2.5mm for

Load bearing sections & 3.0mm for Gland Plate.

- Paint Shade	:	EXT: RAL – 7035

INT: Glossy White

- Paint Thickness	:           Min 80 – 100 Microns

- Protection	:	IP – 42

- Cooling	:	Natural (OR) Forced Air Cooling

- Temperature range	:	0 °C to 50°C

of operation

- Earth Bus Bar (CU)	:           25X6 Sqmm (Copper)

- Relative humidity	:	0 - 95% non-condensing.

* * * * *

IMP NOTE:  1) All Live Parts shall be Properly shrouded.

2) Louvers with Wire Mesh & Eye Bolts need to be provided.

3) 20% Spare TBs need to be considered.

4) Phase Barriers need to be Provided for Power & Control Circuits.

5) Charger Cabinet Height shall be 2115 mm only (Max Height).

6) Meters will be of AE / RISHAB / CONSERV Make Only.

CHARGER THEORY

The system consists of two identical Float cum Boost Chargers, with necessary Interconnection Circuit and a Battery Bank. Both chargers are identical in nature & work on the same principle. These chargers are rated to meet the requirement of Load and Battery charging current as specified.

The Float cum Boost chargers - 1 & 2 are connected to the AC input power through (Q 401/501). The Input transformer (T 401/501) steps down the input AC Voltage to the required level and is connected to the rectifier bridge (SCR 401-406/501-506) through Fast acting Semiconductor Fuses (F 401-402/501- 502). PC 402/502 are capacitive filter Boards that protect the system from surges and transients at AC Input. The charger control board PC 401/501 provides gate signals to these SCRs at appropriate timing depending on the output voltage/current feedback. The Rectifier DC is connected to DC filter (L 401 / 501 and C 402 / 502) which in turn filters out all harmonics and provide DC voltage with low ripple content as specified. The Blocking diodes (V 401/501) prevent reverse current flow into the charger. The output voltage of Float cum Boost Charger is adjusted using the potentiometer R 401-402/501-502 respectively.

The shunt SH 401/501 provides current feedback to charger control board (PC 401/501), which causes the unit to go into current limit, when the load current (charging current) is more than set value.

The Rectifier DC is connected to DC filter (L 401 & C 402/L 501 & C 502) which in turn filters out all harmonics and provides DC voltage with low ripple content as specified.

The meter P 401/501 with shunt, SH 401/501 provides the current feedback to the charger control Board PC 401/501, which causes the unit to go into current limit beyond the set value. This Characteristics cause the output voltage to go down when the battery is run down, to maintain a constant level of charging current.

The DC Ammeter P 401/501 is connected at respective charger output to monitors the charger output currents. The Battery center zero ammeter P2 connected at Battery path monitors the Battery Charge/Discharge current. The DC voltmeter P5 measures the voltages at FCBC- 1,2/Load/Battery through selector switch (S1). The AC ammeter P403/P503 connected at respective charger input monitors the AC input current through selector switch (S 401 & 501). The AC Voltmeter P 402/P502 connected at respective charger input monitors the AC input Voltage through selector switch (S 401 & 501)

The system is provided with Alarm Annunciator (Fascia Display Indicators) for different operating conditions. An Audio Alarm is provided which can be heard during any fault conditions. All Fault Conditions and Indicators are derived through Fascia Display (FD 1) and One set of potential free contacts “GROUP ALARM” is wired up to terminal blocks for remote monitoring purpose. The Fascia display consists of triggering and reset circuit for alarm. For any indication of fault condition, this Fascia display supplies power to the corresponding LED and activates the alarm for faulty condition.

Pressing the ACCEPT Push Button (PB 2) can disable the alarm but enables the indication unless the fault is rectified. TEST Push Button (PB 1) is provided to test the healthiness of the indicators and RESET Push Button (PB 3) is provided to reset the faulty indication after rectification of the fault.

During normal operation, Charger – 1 & 2 will supply the load current as well as float charge the battery. The current interface board (PC 3) connected across Battery shunt terminal provides Battery Charging current limit protection when both chargers are operating in Float mode.

Provision is there to select FCBC-1/FCBC-2 to supply both load current and simultaneously to charge the battery in Float mode. Provision is also available to select one FCBC to supply load current and the other to supply battery charging current. This is achieved by switching on the respective charger and respective mode selector switch in the desired position.

The Tap cell of the battery bank is connected to positive DC bus through tap cell Diode V 1.

## PRINCIPLE OF OPERATION

Both FCBC-1 and FCBC-2 are connected in parallel to battery & load through contactors (K 1/2). During normal operation, both these chargers are kept in FLOAT mode, (i.e., by selecting the respective mode selector switches (S 402/501) in 'FLOAT' position) so that they supply load current as well as trickle charging current to Battery Bank through contactors K 1 & K 2.

Whenever battery requires boost charging, any one of the chargers either FCBC-1 or 2 will switch over to boost mode where it’s respective Power Contactor K 1 or 2 gets opened automatically thereby separating the battery path and load path and this makes the charger in float mode to get connected to the load and the other (in boost mode) to the battery. During this changeover, there will be some interruption (in milli seconds) to load which will be taken care of by the Tap cell of the battery bank. This charger is designed in such a way that boost voltage never reflects on the load and there will be no interruption to the load at any point of time.

During normal Boost mode operation, if both chargers fail, then the total Battery Bank will be connected across the load, through contactor K 1 & 2. The changeover of FCBC-1/FCBC-2 from float mode to boost mode & vice versa will be made automatic and manual selectable through mode select switch S 404/502. The load will be supplied by tap cell through diode during closing and opening of Contactors K 1 & 2.

Provision is available in the system to select Float/Boost mode of operation, automatically, when the respective charger is kept under ‘AUTO’ position in S 402/501. This is achieved auto master current detector board (PC 1) with associated relay boards (PC 2, 404 & 504) and K 403/503.

The system consists of two Float Cum Boost Chargers and all this setup is accommodated in a single panel or two depending on the Rating of Battery Charger System.

Input and output ON/OFF Circuit Breakers are provided separately for each Charger.

On the DC side, the load and battery is connected through Contactors K 1&2. These contactors are normally in closed position (i.e. in energized condition), connecting both load and battery to FCBC-1 and FCBC-2 operating in parallel.

Each Charger is provided with mode selector switch (S 404 & S 502), to select the charger mode of operation with following positions.

Pos. 1: AUTO

Pos. 2: MANUAL FLOAT

Pos. 3: MANUAL BOOST.

One can independently select any of the chargers to the required position and that charger will operate in the selected mode, when the other charger is ON and supplying the load requirement.

Otherwise, it will operate in FLOAT mode only irrespective of Switch Position. This interlock is provided to avoid Boost Voltage reflecting on the load bus.

POS. 1: In this position, the Charger will operate in FLOAT mode and also in parallel with the other charger, supplying both load and battery trickle current. If the Battery Charging current is more than the preset value, then the charger will automatically go into Boost mode, and this will happen when the other Charger is in FLOAT mode. The respective Boost mode charger will be isolated from the other charger and the load. The Boost mode charger will come back to FLOAT mode, once the Charging current comes down less than preset value and it will be reconnected to the other charger and load through contactor K 1/2.

POS. 2: In this position, the Charger will operate in parallel with the other charger if that is also in FLOAT mode and supplies load current and battery current. During this mode both Output Contactors will be in closed position.

POS. 3: In this position, the selected charger will go to BOOST mode and supply the Charging current, and this happens only when the other Charger is supplying load current. During this Boost mode, the respective output contactor K 1/2 will be in an open position separating the battery path and load path that makes the load not seeing any boost voltage. The Boost charging will continue up to the time that is set in the timer and once this set time is completed, the charger will come to float mode and shares the load and battery charging currents.

SPECIAL NOTE:   THIS DUAL FLOAT CUM BOOST CHARGER SCHEME

(2 CONTACTOR LOGIC) CAN BE USED WHERE ONLY FLOAT VOLTAGE NEED TO BE REFLECTED ON LOAD BUS.

## The Status of Charger 1 and 2, Output Contactors K 1 & 2 at various positions are explained in the below Interlocking scheme table for clear understanding:

| INTERLOCKING OPERATION |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| System Condition | Charger Mode Select Switch Position | FCBC– 1 | FCBC– 2 | K-1 | K-2 | Battery | Load |
| Mains Avail |  | FCBC –1 & 2 on Float | ON | ON | ON | ON | On Float (Irrespective of Battery Charging Current) | Supplied by FCBC-1&2 |  |
| Mains Avail |  | FCBC-2 on Float & FCBC-1 on Auto | ON | ON | ON | OFF (or) ON, based on battery charging current, when Boost mode Selected | Supplied by FCBC-1 (on Float/Boost based on Mode select switch position & current drawn by Battery) | Supplied by FCBC-2 when batteries are under Boost Mode. Otherwise FCBC-1& 2 share the Load |  |
| Mains Avail |  | FCBC-1 on Float & FCBC-2 on Auto | ON | ON | OFF (or) ON, based on battery charging current, when Boost mode selected | ON | Supplied by FCBC-2 (on Float/Boost based on Mode select switch position & current drawn by Battery) | Supplied by FCBC-1 when batteries are under Boost Mode. Otherwise FCBC-1 & 2 share the Load |  |
| Mains Avail |  | Any position of Mode selector switch in FCBC –1 & 2 | FAIL | ON | ON | ON | On Float | Supplied by FCBC-2 |  |
| Mains Avail |  | Any position of Mode selector switch in FCBC –1 & 2 | ON | FAIL | ON | ON | On Float | Supplied by FCBC-1 |  |
| Mains Avail |  | FCBC-1 on Float & FCBC-2 on Boost | ON | FAIL | ON | ON | FCBC-1 gets connected to the Battery | Supplied by FCBC-1 |  |
| Mains Avail |  | FCBC-1 on Boost & FCBC-2 on Float | ON, comes to Float mode from Boost /Float mode, Irrespective of Battery Charging current | FAIL | ON | ON | FCBC-1 on Battery | FCBC-1 gets connected to load Battery will supply the momentary load current through tap cell diode. |  |
| Mains Avail |  | FCBC-1 on Boost & FCBC- 2 on Float | FAIL | ON | ON | ON | FCBC-2 gets connected to load | FCBC-2 on load |  |
| Mains Avail |  | FCBC-1 on Float & FCBC-2 on Boost | FAIL | ON, comes to Float from Boost / Float mode, irrespective of Battery charging current | ON | ON | FCBC-2 comes to Float mode, irrespective of charging current | FCBC-2 gets connected to load. Battery will supply the momentary load current through tap cell diode |  |
| Mains Fail |  | Irrespective of switch positions | OFF | OFF | ON | ON | ON Discharge | Battery will supply the load |  |

# TECHNICAL DEVIATIONS / JUSTIFICATIONS

==========================================================================

S. No.	Clause No.	Deviation / Justification

==========================================================================

- Chargers	     	Charger will be Analog type with integrated circuits. The charger will			be SCR/Thyristor Based, 3 Phase, 6 Pulse & Full Wave, Full				Controlled.

- 3 Codes & Standards		All the Components used in designing the Battery charger will be				strictly as per IS / IEC Standards.

- 5 Battery Charger		Battery Charger scheme & Operation will be as mentioned in TSP.

1X 100% DFCBC-2CL Suitable for 1X 100% 220V VRLA Battery

Considered. Process of Changeover from Float to Boost & Vice versa

will be derived through Amara Raja Make PCBs.

- 5.3 General			Battery Charger Designed as per Design Parameters mentioned in Requirements		GTP. No Over Loads Considered (125% & 150% mentioned in Spec)

- 4.2 Design basis		Battery Charger Scheme will be DFCBC – 2CL as mentioned in TSP.

& Sizing Criteria 		the Charger Operation & Working will be as per Operation Logic					mentioned in TSP.

- 5.4 Accessories		Instead of AC Contactors with Thermal Overload Relays, MCCBs					with O/L & S/C Protection Considered. Hence AC Contactor & Relay				are not Providing in System.

- 9.1 Construction		Battery Charger will be housed in suitable Cabinets of Free standing,			Floor Mounted, Sheet steel construction of Thickness 2.5mm for load			bearing & 2.0mm for non-load bearing sections & 3.0mm for gland				Plate. PU Foam gaskets will be used. IP-42 Protection is Provided.

- 8 Tests		All the Routine Tests will be as per our standard QAP Submitted.	(8.1 Type Tests,		Reference Type Test Report will be provided for Charger Only.		& Routine Tests)		Type Testing of Charger & Type Test Charges Not Considered.

- 5.4 Accessories		Amara raja Own make PCBs will be provided for Earth fault	 			protection Instead of high impedance relay.

- 7.0 Battery		220V-510AH VRLA Battery of 110Cells Considered Since Nearest

Available Battery AH Rating.

- 5.6 Annunciation		Thyristor/Diode Failure annunciation can’t be compiled. All the				Protections, Indications & Alarms shall be strictly as per the TSP				only.

- 5.6 Annunciation		All the Alarms & Indications will be as mentioned in TSP. 20% 				Spare Annunciation windows with Accessories Not Possible as all the			windows were already used.

Note: Above all this Offer is strictly as per above mentioned TSP only and any change Will lead to price implication.

  - Type Testing & Type Test Charges Not considered.

  - The Components used to design the Charger System will be as per IS / IEC standards only.

  - Voltage to the Load will be Float Voltage always (220V DC +/- 5%) only.

  - System Concept will be as per specified above. We will be providing Dual FCBC – 2CL.

Special Notes:

- All indications, alarms and protections are derived through Amara Raja make PCB cards which will be built with PLA / OEN make Aux. relays. Hence no other special relays will be used.

- Interconnection cables, Cable Glands & Cable Lugs etc. are not in Amara Raja scope of supply. If required, we can suggest the required cable size.

- All components used in the Charger will be as per the Amara Raja standard sub vendor list specified below.

* * * * *

IMP NOTE: Make of Components will be strictly as per the AMARA RAJA SUB			VENDOR List Only.